## Intro
Introduction | Multisite connects multiple Dynalite based projects to the Cloud allowing end users to monitor them as well as configure Schedules & Scenes through a single dashboard. This document will assess the Multisite commissioning process. Engineers can use it for validating their job, as Systems&Services will use it to confirm everything is in place before handovering the project to the customer. The goal of the Validation tests is to avoid any misconfiguration that will impact the expected behavior at a later stage.
General Procedure | Validation tests should not be performed unless the system has been fully installed and commissioned and, hence, all lighting and associated monitoring and control system components should be in full working order. However, if any genuine faults are witnessed before or during testing, a C4CS support ticket should be raised to System Experts. During the Validation tests, the Project Template form will be used as a reference to what was agreed with the customer during the design&definition phase.
System overview | It is useful for the test witnesses to remember that commissioning is done through three different tools: - System Builder (SB) - Multisite System Manager (MSM) - Philips Dynalite Enabler app (PDE)

## MSM
Multisite System Manager (MSM) cloud dashboard
ID | Task | Test Procedure Description | Expected Result | Resource | Result
1 | Assets tab: Site List | In the Site list table ensure information is correct for the site: - Number of connected light points​ - Site assignment to a proper format​ - Subscription status​ - 4G connectivity status (only for sites with dedicated 4G modem)​ - Site health / online status​ - Operational status (work order status) ​ - Deployment status​ | Ensure the following information is correct: - Number of connected light points​ should match what's on SB and aligns with lighting design. - Site is assigned to a proper format​. - Subscription status​ should be ticked. - 4G connectivity status should be Active (only for sites with dedicated 4G modem)​. - Site health should be green, meaning online status​. - Deployment status​ should be ticked. - Operational status should be in progress if the workorder is still open, or green if resolved. |  | PASS ☐ FAIL ☐
2 | Assets tab: Specific Site View | Select site from the previous table, and ensure information is correct: Overview page: - Site name - Site online status (dot on the left side of a site name) - Site address - Local date and time Suscription: - Type of license & features (Multisite)​ - License status and expiration date​ Deployments&Scenes: - Running deployment, concept and schedule - Properness of scheduled scenes - Properness of an active scene - Properness of next upcoming scenes and time Settings page: - Offset settings for Sunrise and Sunset - Total Floor Area in m2 | Ensure the following information is correct: Overview page: - Site name follows the naming convention - Site online status is green - Site address matches the one on the Project Template form. - Local date and time suits the Site location. Suscription: - Type of license & features should explicitly mention: Multisite. - License status should be Active and expiration date​ should be at least close to 1 year or more, and not close to the 3 months of commissioning grace time. Deployments&Scenes: - Running deployment, concept and schedule. - Properness of scheduled scenes according to deployed schedule. - Properness of an active scene according to light levels. - Properness of next upcoming scenes and time according to deployed schedule. Settings page: - Offset settings for Sunrise and Sunset should match the ones from Project Template form. - Total Floor Area in m2 should be different to 0 , matching either the input from the customer or AutoCAD, or the System Builder estimation. If the last option is chosen, ensure the scale was set properly and that drawn Areas cover the real areas. |  | PASS ☐ FAIL ☐
3 | Energy tab: Dashboard | Check if from the date of first deployment onwards (including current date) the commissioned site is producing Notional (and optionally, Metered Energy). | Energy data should be represented. Note: a preset must be sent to the network either by scheduler/MO/SB for the system to produce data. You may need to wait before you can see some data. |  | PASS ☐ FAIL ☐
4 | Energy tab: Site list | Check both: - Value of KWh / light points for consumed and saved energy. - Value of Wh/m2 for consumed and saved energy. | Values should be possitive and different than n.a. |  | PASS ☐ FAIL ☐
5 | Configuraiton tab: Areas, Scenes & Channels | Review the configuration of the following elements: - Parent Area numbers, names, day&night mode​​. - Scene names, numbers - Child Area numbers, names​​. - Channel numbers, names, type. | Configuration should match the one in the Project Template PDF document. |  | PASS ☐ FAIL ☐
6 | Configuraiton tab: Smart Meter Groups | Ensure that Smart meter groups are configured as per design: - Q-ty of smart meter groups​​ - Smart meter groups naming​​ - Assignment to all or specific format(s).​ | Configuration should match the one in the Project Template PDF document. |  | PASS ☐ FAIL ☐ N/A ☐
7 | Ligth control tab: Concept | Make sure a Default concept is created with the correct information: - Name - Channel levels in all scenes - Day/night mode enablement - Day/night mode channel levels | Concept should follow the naming convention. It should also be tagged as Default and fully applicable for the commissioned Site. Cross check concept vs customer requirements . |  | PASS ☐ FAIL ☐
8 | Ligth control tab: Schedule | Make sure if a Default schedule is created with correct information: - Name - Type of schedule (Regular, Special day, Holiday) - Start/end date of schedule. - Occurrence (Days/Months) - Parent Areas - Schedule actions (including check of fade time) and intervals. - Schedules with actions created for entire week | Schedule should follow the naming convention. It should also be tagged as Default and fully applicable for the commissioned Site. Cross check schedule vs customer requirements and expected store opening/closure. Ensure created schedule include days when store is closed (e.g.: on Sunday) and prevent having duplicates or overlapping schedules. |  | PASS ☐ FAIL ☐
9 | Ligth control tab: Deployment | Make sure if Deployment is created with correct information: - Name - Deployed Default concept and schedule - Deployment status | Deployment should follow the naming convention. Concept and Schedule should be fully applicable for the commissioned site. Status should be set as: Success. |  | PASS ☐ FAIL ☐

## PDE
Philips Dynalite Enabler app (PDE)
ID | Task | Test Procedure Description | Expected Result | Resource | Result
10 | Validate Site installation | Check each Channel, Check each Child Area, Check each Parent Areas, Check finalized Site installation | A green tick before each Channel, A green tick before each Child Area, A green tick before each Parent area, A green tick before “Validate site installation”. | #VALUE! | PASS ☐ FAIL ☐
11 | Validate Deployment​ | Check if deployment of default Schedule and Concept has been done. | A green tick before "Concept and Schedule", A green tick before “Deploy concept and schedule”. | #VALUE! | PASS ☐ FAIL ☐
12 | Validate deployed scenes and concepts | Check each Parent Area, check if all deployed Scenes have been validated. | A green tick before each Parent Area, A geen tick before “Validate concept and schedule”. | #VALUE! | PASS ☐ FAIL ☐
13 | OTRS tickets | Customer has access to the system. | User account for the customer is created via OTRS ticket, with Format or the Facility Manager as specified in Project Template form. |  | PASS ☐ FAIL ☐

## SB
System Builder (SB)
ID | Task | Test Procedure Description | Expected Result | Resource | Result
14 | Remote connectivity test | Open your project in System Builder and connect remotely using Online Gateway Connection. | System Builder should be able to sign on devices remotely. |  | PASS ☐ FAIL ☐
15 | Area View | Check Parent and Child areas, Channels, Presets numbers, and naming. | They should be the same than the Cloud configuration​ and the Project Template PDF. Ensure all Child Areas have outputs in Channel 1. |  | PASS ☐ FAIL ☐
16 | Base Link Area | Ensure all Outputs within the Child Areas use Base link areas​ to their Parent Area. | Base Link Area should be equal to the corresponding Parent Area (e.g. Area 21 will have BLA = 2). |  | PASS ☐ FAIL ☐
17 | Presets | Ensure Presets are created. | There should be 64 presets per Area as well as per controller output. Presets should be synchronized from Logical to Physical. |  | PASS ☐ FAIL ☐
18 | Installed power | For each load controller, check all outputs have the proper Load (Watts). | For used channels, value should correspond to the installed load, usually a possitive value different than 0 with the exception of special luminaires with 2 drivers where one is dedicated for emergency, which should be set as 0 only for emergency. |  | PASS ☐ FAIL ☐
19 | Gateway configuration | For the PDDEG-S ensure: Device Properties - Batch reporting Schedules - Location & Time Zone Ports - IPv4 and IPv6 settings Routing - Route RS485 and default Multicast service Tasks (optional) Retail Manual Override and Alarm task template. BACnet (optional) - BACnet service | For the PDDEG-S ensure: Device Properties - Batch reporting must be enabled Schedules - Location & Time Zone needs to be correct. - Also, count 100 active schedules, 30 disabled special events, and 30 disabled holiday events. Ports - For static IP, network settings should be correct (IP address, Subnet address, Gateway address, DNS address, and optionally Secondary DNS address). - Confirm that IPv6 UDP is disabled both for multicast&unicast. Routing - Routing (may vary for 3rd party integrations) should include: Websocket to ComPort, Com Port to Websocket, Internal messages to Websocket, and Metrics collection to websocket. - Route RS-485 and Default Multicast service checkbox should be unticked. Tasks (optional) Retail Manual Override and Alarm task template can be used for Manual Override and Alarm integration. It needs to be properly configured. BACnet (optional) - BACnet service should be disabled, unless BACnet integration is required. |  | PASS ☐ FAIL ☐
20 | Job file timezone | Besides the PDDEG-S Location&Timezone setting, SB job file should have its own Location&Timezone properly configured. | Go to Tools>Set Location and Timezone and check if it's correct. Clicking OK is mandatory to make Job file Time Zone setting effective. |  | PASS ☐ FAIL ☐
21 | BMS & Alarm integration | Check if dry contacts functionality works as expected | Ensure wiring and polarity are ok for alarm integration. It has been proven difficult to validate on the field. |  | PASS ☐ FAIL ☐
22 | Emergency ligjting | If emergency lighting is controlled, ensure at least 2 emergency groups are created. For emergency luminaires represented by 2 drivers on the floor plan – emergency load profile channel load = 0W. Trigger Manual functional test. If desired, push testing schedule to the drivers for periodical automatic tests. | Tests should provide expected results according to the status of the emergency luminaires. |  | PASS ☐ FAIL ☐ N/A ☐
23 | Modbus meters configuration | For each Modbus meter ensure: Device Properties: - Modbus meter is enabled Modbus Configuration Editor: - Active energy register (kWh) should be enabled. - Make sure the Power Zone (Smart Meter Group) is created and assigned to the meter. - For custom meters: validate expected Active Energy consumption vs. Register value indication in System builder. In DDNG485 or EG above the meter check: Total Energy Consumption metric Polling Interval is set to 15 minutes. For all IP meters, check: - Modbus meters connectivity. - EG routing tab needs to be completed. | Device Properties: - Modbus meter is enabled Modbus Configuration Editor: - Active energy register (kWh) should be enabled. - Make sure the Power Zone (Smart Meter Group) is created and assigned to the meter. - For custom meters: validate expected Active Energy consumption vs. Register value indication in System builder. In DDNG485 or EG above the meter check: Total Energy Consumption metric Polling Interval is set to 15 minutes. For all IP meters, check: - Modbus meters connectivity. IP meter address should be unique and on the same subnet than the PDDEG-S. - EG routing tab needs to be completed: IPV4<>Websocket, Internal message>Wesocket, Internal message>IPv4, IPv4<>IPv4, Metrics>Websocket, Internal>Comm Port 1, Comm Port 1<>Websocket, Metrics>IPv4, Metrics>Comm Port. |  | PASS ☐ FAIL ☐ N/A ☐
24 | Physical configuration | All devices in System View need to have unique names according to naming convention. | Ensure names are unique, and otherwise modify it. |  | PASS ☐ FAIL ☐
25 | User interfaces | Ensure Antumbra or PDRP: - Actions should use presets with specific join byte. - UI controlling a Child Area should be linked with the corresponding BLA. | Manual override uses Join byte 0x83. BLA should match the Parent Area. |  | PASS ☐ FAIL ☐
26 | PDTS | Ensure PDTS: - PDTS buttons should use presets with specific join byte. - UI controlling a Child Area should be linked with the corresponding BLA. - Schedules shouldn't be configured on the PDTS. | Manual override uses Join byte 0x83. BLA should match the Parent Area. |  | PASS ☐ FAIL ☐
27 | Sensors | Ensure sensors: - Use the specific join byte according to functionality. - Are calibrated for daylight harvesting, and if Open Looped is used that bands are estimated properly. - Traffic is reduced by using the maximum Update period on sensors dedicated for light control - Motion Detection or Light control configured for a Child area should be linked with corresponding BLA. | Motion Control should use join 0x81, while daylight harvesting uses join byte 0x82. |  | PASS ☐ FAIL ☐
28 | Dry contacts | Ensure dry contacts: - Use the specific join byte according to functionality. - Unused dry contacts are set to No function to avoid messges on the network. | Alarm integration should use join 0x85. Make sure polarity and wiring is done as per design. |  | PASS ☐ FAIL ☐
29 | Custom Tasking configuration | Ensure: - Traffic is minimized by usage of Presets to BLA. - Preset actions use the corresponding join bytes. - Logic does not creates infinite loops | Avoid using ChannelLevel or sending Presets to all Child Areas. Instead, use Preset message to Parent Areas. Make sure Join bytes configuration​s are correct: - For motion related events 0x81 - For Day light regulation events 0x82 - For Manual Override actions 0x83 - For Alarm/BMS integrations 0x85 |  | PASS ☐ FAIL ☐
30 | Total Floor Area | From Job Properties, ensure Size Site (m2) field is filled with the correct data. | The Site Size field (m2) in SB should be filled either with the Area estimation from System Builder, or with the input from the customer or AutoCAD. If estimation from System Builder is used, ensure Areas are accurately drawn and scale is properly set. |  | PASS ☐ FAIL ☐
31 | Floor Plan | The Floor Plan should be free of errors. | Ensure there're no exclamation marks on the floor plan |  | PASS ☐ FAIL ☐
32 | Luminaires | Ensure all luminaires are commissioned (indicator in building view). | The amount of luminaires should match the connected lightpoints on the Cloud. |  | PASS ☐ FAIL ☐
33 | PDDEG-S | Network settings: - If PDDEG-S uses dhcp, MAC should be whitelisted on customer DHCP server. Connection and stability: - Check Cloud LED on the PDDEG-S IT customer switch port configurations - Port speed (100mbps) - Duplex: auto - Disabled EEE - Open ports 5671 or detailed list of whitelisted endpoints | Cloud connection: Cloud LED is solid white/green To check it remotely, connect remotely and download MQTT logs to see EG's status Stability: Cloud LED is solid white/green for at least 3 min. To check this remotely, tun endpoints scan at least 3 times in a row. For any concerns, ask SE for checking syslog report. IT customer switch port configurations - Port speed (100mbps) - Duplex: auto (cannot be half) - Disabled EEE - Open ports 5671 or detailed list of whitelisted endpoints |  | PASS ☐ FAIL ☐